## Sheet1
HEAT TRANSFER
MULTIPLE COMPONENT HEAT CALCULATIONS
| INGREDIENT | MASS FLOW | Cp |  | TEMP | DELTA T
|  | LB/HR | BTU/LB-DEG F | BTU/DEG F | DEG F | DEG F | BTU/HR
| A | 1251 | 1 | 1251 | 400 | 100 | 125100 | m x c x delta t
| B | 1076 | 1 | 1076 | 145 | -155 | -166780
| C | 0 | 1 | 0 | 300 | 0 | 0
| D | 0 | 1 | 0 | 300 | 0 | 0
| E | 0 | 1 | 0 | 300 | 0 | 0
| F | 0 | 1 | 0 | 300 | 0 | 0
| G | 0 | 1 | 0 | 300 | 0 | 0
| H | 0 | 1 | 0 | 300 | 0 | 0
| I | 0 | 1 | 0 | 300 | 0 | 0
| J | 0 | 1 | 0 | 300 | 0 | 0
| K | 0 | 1 | 0 | 300 | 0 | 0
| TOTALS | 2327 |  | 2327 | 300 |  | -41680
HEAT TRANSFER THROUGH AN INSULATOR
|  |  | LOSS | 27142.8571 | BTU/HR
|  |  | LOSS | 7.9598 | KW
|  |  | LENGTH | 50 | FT
|  |  | WIDTH | 38 | FT
|  |  | R VALUE | 7 | HR-SQFT-DEG F/BTU
|  |  | U | 0.14286 | BTU/(HR-SQFT-DEG F)
|  |  | K | 2 | BTU-IN/(HR-SQFT-DEG F)
|  |  | DELTA T | 100 | DEG F
|  |  | INSULATION THICKNESS | 14
HEAT TRANSFER IN A SINGLE PASS HEAT EXCHANGER
|  |  | PRODUCT SIDE |  |  |  | UTILITY SIDE
|  | POWER | 630504 | BTU / HR |  | POWER | 700560 | BTU / HR
|  | POWER | 52.542 | TONS |  | POWER | 58.38 | TONS
|  | POWER | 42.0336 | REFRIG TONS |  | POWER | 46.704 | REFRIG TONS
|  | POWER | 184.8985 | KW |  | POWER | 205.4428 | KW
|  | FLOW | 36 | GPM |  | FLOW | 16.4706 | GPM
|  | SPEC GRAVITY | 1 |  |  | SPEC GRAVITY | 1
|  | MASS FLOW | 300.24 | LB / MIN |  | MASS FLOW | 137.3647 | LB / MIN
|  | Cp | 1 | BTU / LB-DEG F |  | Cp | 1 | BTU / LB-DEG F
|  | DELTA T | 35 | DEG F |  | DELTA T | 85 | DEG F
|  | EFFICIENCY | 0.9
SENSIBLE HEAT CHANGE OF A BATCH
|  | ENERGY | 188484 | BTU
|  | TIME | 70 | MINUTES
|  | RATE | 161557.7143 | BTU/HR
|  | RATE | 47.3776 | KW
|  | VOLUME | 113 | GALLONS
|  | SPEC GRAVITY | 1
|  | MASS | 942.42 | LB
|  | Cp | 1 | BTU / LB-DEG F
|  | DELTA T | 200 | DEG F